## Slide 1
Air Handler Filtration
Project Management – Professional Development Series

## Slide 2
  Air Filtration: WHAT, WHY, & HOW?
  Relevant Standards & MERV
  Filter Types On Campus
  Challenges Across Campus
  CU Filtration Standard Updates
Outline

## Slide 3
  Air filtration: WHAT, WHY, and HOW?
WHAT is a filter?
  Devices comprised up of:
  Metal, plastic, or cardboard frames
  Organic or synthetic media

## Slide 4
  Air filtration: WHAT, WHY, and HOW?
WHY do we filter air?
  Captures particulates (dust, mold, viruses)
  Protects occupants
  Protects equipment

## Slide 5
  Air filtration: WHAT, WHY, and HOW?
HOW do we implement?
  Pre-Filters
  Primary-Filters
  Final-Filters

## Slide 6: Relevant Standards
Old – ANSI/ASHRAE 52.1 “dust spot” efficiency
  Percentages
  85% filter – captures 85% of 1 micron particles
  1 micron
    Coal dust
    Anthrax

## Slide 7: Relevant Standards
New (2009) – ANSI/ASHRAE 52.2
  MERV (Minimum Efficiency Reporting Value)
  MERV 13 equates to 85%

## Slide 8: Relevant Standards
ANSI/ASHRAE 52.2

## Slide 9: Filters Cornell Uses
Pleated (1”, 2”, 4”, 12” deep)
Panel (1” deep)
Cassettes (12” deep)
Pocket Filters (15”, 22”, 30” deep)
Commercial & Industrial – C&I (1” deep)

## Slide 10: Sizes
So, so many…
24x24, 24x12, 25x20, 25x16, 20x20, 20x16, etc., etc., etc…
There’s a real need to standardize sizes
  Reduces strain on procurement team and mechanics

## Slide 11: Sizes
Reality – Standardization not so easy.
  Too many small terminal units with non-standard filter sizes
  Especially when utilizing C&I pleated filters
    7”x66”…
Good news is 99% of building AHUs from the 90s to Now utilize 24” x 24” and 24” x 12” filters.

## Slide 12: Current Filtration Challenges
Older Air Handlers
  One filter rack
  Shallow filters (1” or 2”)
  Lower MERV (8)
  Leaky filter racks (air bypass)

## Slide 13: Current Filtration Challenges
Snow/Rain/Cottonwood Entrainment
  Clogs filters
  Mechanics scramble during harsh weather
  Synthetics and snow screens help mitigate failures

## Slide 14: Current Filtration Challenges
Upgrading to higher a MERV rating
  Higher resistance to flow
  Requires more horsepower to maintain airflow
  Could lead to lower airflow in AHUs without VSDs
  Increase in replacement costs

## Slide 15: Cornell Filtration Standard
Pertains to New Installations, Only
MERV 13 for all typical occupancies
Previously
  Offices/Classes MERV 11
  Laboratories MERV 13
Current
  LEED MERV 13
  All MERV 13

## Slide 16: Cornell Filtration Standard
Additional standardization language
  Smaller Units
    16” x 16”
    16” x 20”
    16” x 24”
    16” x 25”
    18” x 24”
    18” x 25”
    20” x 20”
    20” x 24”
    20” x 25”

## Slide 17: Cornell Filtration Standard
Additional standardization language
  Type – Cassette vs. Pocket
  vs.

## Slide 18: Cornell Filtration Standard
Application-specific snow screen language

## Slide 19
Thank You!