## Slide 1
Proposed Changes Cornell Design and Construction Standard 018110 Energy Efficiency and Sustainable Design Standard (formerly 018110 Green building guidelines)
Matthew Kozlowski
Facilities Engineering
October 2022

## Slide 2
Who were the primary authors/editors?
Erik Eshelman, Elizabeth Kolacki, Cole Tucker, Mark Howe, myself were primary authors.
Why are we updating the standard?
The green building last had a major overhaul almost a decade ago.
Alignment with new codes and requirements (IECS, NYC Energy Roadmap).
Applying lessons learned.
Major Shifts:
Actions vs. Targets – More emphasis on prescriptive and code-based actions (Stretch Code, leak sealing, commissioning) vs. EUI and modeled energy usage requirements.
Tiered approach – Captures lower dollar threshold (<$5M) projects that are ignored in current standard.
Pushes goal setting out of standard language (where it is too late to implement) and towards the project charter stage.
Draft 018110 Energy Efficiency and Sustainable Design Standard

## Slide 3
Designs must comply with NYStretch Energy Code (IECS).
Commission all new HVAC, Service Water Heating, and Lighting/Electrical systems. May be completed by project team or in-house if appropriate.
Preparation of a basic energy model. (Consistent with current standard, IECS)
Evaluate opportunities for renewable energy integration. (Consistent with current standard, IECS)
Seal envelope leaks within the project area.
No new natural gas infrastructure. No direct replacement of natural gas equipment without evaluating electrification or district energy connection (IECS).
<$5M total project cost

## Slide 4: $5 - 10M total project cost
Achieve LEED SIlver
Consider envelope upgrades
All requirements for projects under $5M
Consider LEED Gold
All requirements for projects under $10M
>$10M total project cost

## Slide 5: Please Let me Know Your Thoughts!
Please contact me with questions or comments! – Matt Kozlowski - MDK39
Full text copy of the draft revision is on box. You are invited to review and comment! Just let me know if you want access.
I am targeting publishing the new standard in the first week of November.

## Slide 6: Alignment with Ithaca Energy Code Supplement
Criteria | Old Standard | New Standard | IECS
Energy Use Reduction Targets | 30% modeled energy use reduction Energy Use Intensity targets | With IECS as the City/Town code, energy targets are set by code. CU requirements are redundant. | Requirement to hit targeted percentage reduction (40/80%) or point based system corresponding to energy use reductions.
NY Stretch Code | -- | Requires NY Stretch Code for all projects | Awards points for utilizing stretch code.
Basic Energy Model | Required | Required | Required to document energy targets under both modeling and point-based paths.
Natural Gas Equipment | -- | Prohibits new infrastructure. Requires study when replacing existing uses and encourages electrification | Heavily favors electrification for heating, service water, and cooking and provides points under point-based paths.

## Slide 7
Section | Description | Discussion
Formatting | Clarified prescriptive and suggested actions (“should/shall”) throughout. Inserted variance language. Deleted example contractor matrix and submittal cover form. | NA
Objectives (Section 1.02) | Simplifies objectives language. Deletes problematic EUI target language. Existing EUI language was typically unobtainable. NYS/IECS code has advanced energy performance requirements by code to sufficient degree that specific EUI language is unnecessary. | Code/LEED provides sufficient requirements for energy performance. Eliminating the specific target reduces the redundant energy targets.
 | Deletes minimum percentage reduction for energy modeling. NYS/IECS code has advanced energy performance requirements by code to include a baseline that makes compliance with our old % based standards very difficult and at times impossible to achieve. | Code/LEED provides sufficient requirements for energy performance. Eliminating the specific target reduces the redundant energy targets.
 | Requirement for renewable energy (solar ready) adoption/discussion is included in NY Stretch Code (see Section 2.01) | NA
Quadruple Bottom Line (Section 1.06) | Provides suggestion that project major decision points incorporate Cornell Quadruple Bottom Line evaluation framework and provides link to CU process link. | Optional requirement that provides access to often overlooked CU decision making matrix.
Detailed list of Changes

## Slide 8
Section | Description | Discussion
Determining Goals (Section 2.01) | Previous standard did not have specific requirements for projects under $5M in total cost. This creates tiered requirements for projects under $5M, $5M-$10M, and >$10M. | Creates a tiered approach that captures projects less than $5M in project cost. Previously these projects had little or no energy/sustainability requirements. We have targeted modest, easily implemented and obtainable requirements based on best practice to address these projects.
 | Requires all projects to be designed using the NY Stretch Energy Code (a supplement to the NYS ECC). | Requires projects be solar and EV “ready” if applicable, and to incorporate air barrier requirements. This code supplement has been adopted by many municipalities (including Dryden) and is awarded "points" under the Ithaca energy code supplement.
 | Requires all projects to comply with energy and sustainability goals established in the project charter. | Sustainability goals need to be established sooner in the project planning process. By the time the Architect contract is issued and the Design and Construction Standards come into play, we have lost an opportunity.
 | Requires that ALL new HVAC, service water heating, and lighting/electrical systems be commissioned. Teams can use in-house commissioning if applicable. Typically only large projects are commissioned, and these use third-party agents. | System commissioning ensures that newly installed systems are operating as designed, and prevents new systems from unbalancing existing building energy systems. Currently only large (LEED) projects are required to hire a third-party commissioning agent. The requirements allow for internal commissioning by CU staff or project team members when appropriate.
Detailed list of Changes

## Slide 9
Section | Description | Discussion
Determining Goals (Section 2.01) | Requires all projects impacting building energy use to perform a basic energy model. Goal for all existing building projects to keep energy consumption flat compared to existing usage, and identify offsetting actions to mitigate any increases. | A basic energy model is required to at a minimum, understand load impacts to the facility. At a minimum, we have set the goal to keep energy usage in existing buildings flat (ideally reduced), and identify/document actions that offset increases to keep energy use flat.
 | All projects in existing spaces shall seal envelope leaks. | Sealing the building envelope presents a low-cost, high impact opportunity for projects in existing buildings.
 | Projects shall not install new natural gas uses or infrastructure. Projects shall make every effort to eliminate existing uses of natural gas. Direct replacements of equipment shall require evaluation for conversion. | NA
 | Projects greater than $5M shall investigate building envelope improvements. | NA
 | Projects greater than $10M shall consider achieving LEED Gold at a minimum. | NA
Detailed list of Changes